USER MANUAL

IoT-Based Prepaid Sub-Metering System for Shared Residential Hostels

## Document Information

| Project Title | IoT-Based Prepaid Sub-Metering System |
| --- | --- |
| Version | 1.0 |
| Date | 19th August 2026 |
| Authors | Pearl Acquah, Edward Boansi |
| Institution | University of Cape Coast |
| Department | Department of Computer Science and Information Technology |

# 1. Introduction

## 1.1 Purpose

This user manual provides instructions for operating the IoT-Based Prepaid Sub-Metering System. The system is designed to monitor and manage electricity consumption in student hostels, enabling fair and transparent billing through prepaid credit management.

## 1.2 Intended Users

| User Type | Description |
| --- | --- |
| Hostel Administrators | Manage the system and monitor consumption |
| Students/Residents | View consumption and credit status as well as top-up credit |

## 1.3 System Capabilities

Real-time Monitoring — Voltage, current, power, and energy consumption measurements.

Prepaid Credit Management — Pay-before-use credit model.

Automated Disconnection — Instant power cut off upon credit exhaustion.

Remote Top-up — Credit addition via web dashboard.

Transaction History — Complete audit trail of top-up operations.

Independent Room Control — Isolated monitoring and control per room.

# 2. Safety Precautions

⚠️ WARNING Failure to follow these safety precautions may result in serious injury, electric shock, or death.

## 2.1 Electrical Safety

| Precaution | Description |
| --- | --- |
| Disconnect Power | Always disconnect the system from AC mains before performing maintenance or wiring changes. |
| Proper Enclosures | All AC components must be housed in approved electrical enclosures. |
| No Bare Wires | Ensure no exposed copper wires are present. |
| Fuse Protection | Use appropriate fuses on all AC connections. |

## 2.2 General Safety

| Precaution | Description |
| --- | --- |
| Dry Environment | Keep the system away from water and moisture. |
| Ventilation | Ensure adequate airflow around components. |
| No Obstruction | Do not block ventilation holes. |
| Children | Keep the system away from children. |
| Power Cord | Do not damage or modify the power cord. |

# 3. System Overview

## 3.1 Component List

| Component | Description | Function |
| --- | --- | --- |
| Arduino Mega 2560 | Main controller | Processes data, controls relays |
| PZEM-004T v3.0 | Energy sensor | Measures Voltage, Current, Power, Energy (kWh) |
| 2-Channel Relay Module | Power switch | Controls AC power feed to designated rooms |
| Web Dashboard | User interface | Displays live data and handles credit top-ups |

# 4. Hardware Setup

## 4.1 Arduino to PZEM Connections

| Arduino Mega Pin | PZEM-004T Pin | Wire Colour |
| --- | --- | --- |
| 5V | VCC | Black |
| GND | GND | White |
| Pin 18 (TX1) | RX (PZEM 1) | Grey |
| Pin 19 (RX1) | TX (PZEM 1) | Purple |
| Pin 16 (TX2) | RX (PZEM 2) | Red |
| Pin 17 (RX2) | TX (PZEM 2) | Yellow |

## 4.2 Relay connections

| Arduino Mega Pin | Relay Pin | Wire Color |
| --- | --- | --- |
| 5V | VCC | Black |
| GND | GND | White |
| Pin 4 | Relay 1 | Grey |
| Pin 7 | Relay 2 | Purple |

## 4.3 CT Clamp Installation Steps

- Turn off and safely isolate the main supply to the circuit before touching any connections.

- Identify the Live wire supplying power to the target room.

- Carefully loosen the terminal screw and disconnect the Live wire from its terminal block.

- Position the clamp around the Live wire only.

- Pass the free end of the Live wire through the center of the ring CT.

- Ensure the directional arrow on the clamp points TOWARD the load (away from the supply source).

- Re-insert the Live wire back into its terminal block/breaker and torque it securely.

# 5. Software Setup

## 5.1 Web Dashboard Deployment Steps

Open Command Prompt as Administrator.

Navigate to the project directory: cd "C:\Users\Administrator\Desktop\Prepaid dashboard"

Execute dependency installation: npm install

Launch the backend server: npm start

Open web browser and navigate to: http://localhost:3000

# 6. Troubleshooting

| Problem | Possible Cause | Solution |
| --- | --- | --- |
| No dashboard readings | Arduino disconnected | Verify USB cable |
| Voltage reads 0.0V | PZEM AC line missing/Loose jumper wire connections | Check AC connections/Inspect, tighten, and re-seat all jumper wires |
| Current reads 0.00A | Loose jumper wire connections | Inspect, tighten, and re-seat all jumper wires |
| Relay un-responsive | Incorrect pin definition | Verify Pin 7/8 connections |
| Dashboard offline | Node server not running | Execute 'npm start' in CLI |

# 7. Technical Specifications

| Component | Specification |
| --- | --- |
| Arduino Mega 2560 | ATmega2560 micro-controller, 256KB Flash, 8KB RAM, 16MHz |
| PZEM-004T v3.0 | Operating Voltage: 80–260V AC, Current: 0–100A, Accuracy: 0.5% |
| Relay Module | 2-Channel, 30A / 250V AC switching rating, 5V trigger |
| Software Stack | Node.js (Backend), Express, HTML5/JS Dashboard |